**Weott CSD’s Operator’s Report**

**9-18-24**

**Kyle and Greg**

**Springs/Flow:** We are still getting flow from A and B springs.

**Test Results:** Water quality has been passing state standards.

**Water Plant:** It has been working efficiently.

**Wastewater Plant:**It is functioning properly and passing state tests.

**Project Update:** We started the project for the new A tank on 7-17-24. They have finished digging the footings for the concrete for the tank . They have installed all the rebar and forms for the concrete. They started digging for the drain system and installing a culvert for proper drainage.

**Lift station:** Pulled one of the pumps at the lift station to see if it might have been seized up but it wasn't. We replaced the contactor coil and the lift station control panel. No difference and it's going to be approximately $500 or $600 to replace it. We might be able to get it repaired.

We Alternated lines at the leach field. None of The wet wells that I checked had any water in them.

**Meters:** While reading meters found a leak on Newton and repaired it.

Also, upon Management's request pulled the connections at 443 Newton.

We Checked the meter at 110A Newton by hooking up a second meter in line with theirs..

There was a 10 gallon difference between the two but not enough to explain the high readings